## Slide 2
Pipe= Flow resistance.
-. Fluid pressure drops through it.
Input (boundary cond.):
-. mass flow rate with ramp in time. Increase it gradually.
-. Inlet temperature with fixed value.
Input (boundary cond.):
-. Outlet pressure with fixed value.
Output of interest:
-. Inlet pressure.
Volumes
-. In order to see the temperature and enthalpy change across the pipe.
Output of interest:
-. Outlet temperature.

## Slide 3
Input:
mass flow rate flowing through pipe.

## Slide 4
Output:
Fluid pressure of pipe inlet.
It increases as mass flow rate increases.

## Slide 5
Output:
Specific enthalpy at inlet.
Output:
Specific enthalpy at outlet.
It is same value as inlet owe to enthalpy conservation.
The “delay” occurs due to volume effect (storage of mass and energy).

## Slide 6
Output:
Temperature at inlet.
Output:
-. Temperature at outlet.
-. It is slightly greater than that of inlet. The energy lost as pressure drop is converted to temperature. Notice flow enthalpy conserves because the energy lost does not go anywhere.
-. Temperature rise occurs only in incompressible fluid (liquid)
-. The temperature difference increases as pressure drop increases.

## Slide 7
pumpingSystem_ex01

## Slide 8
Pipe= Flow resistance.
-. Fluid pressure drops through it.
Measure fluid power of pump.
Figure out mechanical power supplied to pump.
= (fluid power) / eff.
Centrifugal pump
-. Constant efficiency.
-. Mechanical interface is rotational speed signal.

## Slide 9
Input:
mechanical rotary speed of pump.

## Slide 10
Output:
Volumetric flow rate through pump.

## Slide 11
Output:
pump discharge pressure.

## Slide 12
Output:
Pump’s volumetric flow rate vs. mechanical rotation speed.

## Slide 13
Output:
-. (pump.V_flow)*dP
-. Increase in “flow power”
Output:
-. Mechanical power consumed by pump.
-. (pump.V_flow)*dP / pump.eta
-. 2 variables are equal.

## Slide 14
Output:
mechanical power consumption of pump vs. mechanical rotation speed.

## Slide 16
体積流量 [m^3/s]
揚程 [m]
-. 定格回転数における、揚程 vs. 体積流量の特性カーブを与える必要が有る。
-. MSLには２次カーブと多項式カーブを与えるfunctionが用意されている。
pumpingSystem_ex01では最もシンプルな２次カーブを用いる。
*ユーザー定義のカーブfunctionを用いて呼び出すことも可能。
機械回転数 [rpm]
体積流量 [m]
揚程 [m]
{定格回転数, 定格体積流量}
{定格回転数, 定格揚程}
機械回転数 [rpm]
redeclare function flowCharacteristic = Modelica.Fluid.Machines.BaseClasses.PumpCharacteristics.quadraticFlow(V_flow_nominal = {0, 0.25, 0.5}, head_nominal = {100, 60, 0})
定格点のparameterを基に
体積流量=k*機械回転数
として算出(スケール)される。
定格点のparameterを基に
体積流量=k*(機械回転数)^2
として算出（スケール）される。
非定格点の体積流量、揚程の算出
体積流量、揚程の特性の与え方
下記の記述により、特性モデルにMSL収録の２次カーブfunctionを用いることを設定すると共に、２次カーブを成す３点の値をparameterとして与える

## Slide 17
断熱効率特性の与え方
体積流量 [m^3/s]
断熱効率 [nond]
定格回転数における効率カーブを与える。
MSLには効率を一定とするfunctionしか用意されていないため、カーブを与えたい場合はユーザー定義functionを作成する必要が有る。
pumpingSystem_ex01では、簡略化のため、定格回転数における断熱効率を一定とするようparameter設定する。
redeclare function efficiencyCharacteristic = Modelica.Fluid.Machines.BaseClasses.PumpCharacteristics.constantEfficiency(eta_nominal = 0.9)
下記の記述により、特性モデルに効率固定値のfunctionを用いることを設定すると共に、固定値として設定する効率値を与える。

## Slide 18
pumpingSystem_ex02

## Slide 20
pumpingSystem_ex03

## Slide 21
“Prescribed pump” is replaced with “pump”
The valve for flow control is added. The valve type is the simplest one.
The components so as to provide mechanical rotational speed (in [rpm]) to flange connector are added.

## Slide 22
Input:
mechanical rotary speed of pump.

## Slide 23
Input:
opening of linear valve.

## Slide 24
Output:
Volumetric flow rate through pump.

## Slide 25
Output:
Pump’s volumetric flow rate vs. mechanical rotation speed.

## Slide 26
Output:
pump discharge pressure.

## Slide 27
Output:
Mechanical power consumed by pump.

## Slide 28
Output:
Torque into flange of pump.

## Slide 29
Output:
mechanical power consumption of pump vs. mechanical rotation speed.

## Slide 30
Output:
pressure difference of valve vs. mass flow rate via valve.
Increase in pump rotation speed.
Close of valve (from 1 to 0.5).
If pump speed is reduced.
If pump speed is increased.

## Slide 31
PumpAsTurbine_ex01

## Slide 33
PumpAsTurbine_ex02

## Slide 35
-. Flow path consists of 2 pipes.
-. Each pipe is composed of “resistance” part and “capacitance” part.
-. First pipe receives heat from outside of flow path.
-. In this example, it is defined that heat receive occurs AFTER pressure drop of pipe. Definition of BEFORE or AFTER influence on pressure drop because fluid density and viscosity changes.
-. If it is desired that heat receive and pressure drop occurs simultaneously, deploy “DynamicPipe” and define sections as many as possible (Example of “DynamicPipe” will be in “FlowWithHeating_ex02”).
-. Pressure drop in pipe1 is affected by change of density and viscosity due to heat receive upstream.