## Slide 4
-. Flow path consists single pipe.
-. Pipe is composed of “resistance” part and “capacitance” part internally.
-. Pipe has 5 “resistances” and “capacitance”.
-. “Resistance” and “capacitance” lines up one another.
-. Entire pipe receives heat from outside of flow path.
-. Pressure drop and heat receive occur at the same time in single component.
-. Still discretized model. Pressure drops and heat receive occur separately in component.
-. Replicate signal into vector of signal.
-. Heat flow source seems single component. However, there are 5(number of discrete sections of pipe) instances so as to provide heat to 5 heat ports.
-. Divide whole heat flow into pipe by 5 (number of discrete sections of pipe).
-. Place volumes to observe fluid states before and after pipe.

## Slide 8
-. Flow path consists of 2 pipes.
-. Each pipe is composed of “resistance” part and “capacitance” part.
-. First pipe receives heat from outside of flow path.
-. In this example, it is defined that heat receive occurs AFTER pressure drop of pipe. Definition of BEFORE or AFTER influence on pressure drop because fluid density and viscosity changes.
-. If it is desired that heat receive and pressure drop occurs simultaneously, deploy “DynamicPipe” and define sections as many as possible (Example of “DynamicPipe” will be in “FlowWithHeating_ex02”).
-. Pressure drop in pipe1 is affected by change of density and viscosity due to heat receive upstream.

## Slide 9
Input:
Heat flow rate injected into fluid system.

## Slide 10
Output:
Specific enthalpy of fluid in the volume where heat is injected into fluid system.

## Slide 11
Output:
Temperature of fluid in the volume where heat is injected into fluid system.

## Slide 12
Output:
Pressure drop in pipe1 (pipe downstream of heat injection).

## Slide 13
Output:
Density of fluid at the entrance of pipe1 (pipe downstream of heat injection).

## Slide 14
Output:
Fluid density vs. fluid Temperature.

## Slide 15
Output:
Viscosity of fluid at the entrance of pipe1 (pipe downstream of heat injection).

## Slide 16
Output:
Fluid viscosity vs. fluid temperature.

## Slide 17
Output:
Fluid velocity at the entrance of pipe1 (pipe downstream of heat injection).

## Slide 18
Output:
Reynolds number at the entrance of pipe1 (pipe downstream of heat injection).

## Slide 19
PumpAsTurbine_ex02

## Slide 21
PumpAsTurbine_ex01

## Slide 23
pumpingSystem_ex01

## Slide 24
Pipe= Flow resistance.
-. Fluid pressure drops through it.
Measure fluid power of pump.
Figure out mechanical power supplied to pump.
= (fluid power) / eff.
Centrifugal pump
-. Constant efficiency.
-. Mechanical interface is rotational speed signal.

## Slide 25
Input:
mechanical rotary speed of pump.

## Slide 26
Output:
Volumetric flow rate through pump.

## Slide 27
Output:
pump discharge pressure.

## Slide 28
Output:
Pump’s volumetric flow rate vs. mechanical rotation speed.

## Slide 29
Output:
-. (pump.V_flow)*dP
-. Increase in “flow power”
Output:
-. Mechanical power consumed by pump.
-. (pump.V_flow)*dP / pump.eta
-. 2 variables are equal.

## Slide 30
Output:
mechanical power consumption of pump vs. mechanical rotation speed.

## Slide 32
体積流量 [m^3/s]
揚程 [m]
-. 定格回転数における、揚程 vs. 体積流量の特性カーブを与える必要が有る。
-. MSLには２次カーブと多項式カーブを与えるfunctionが用意されている。
pumpingSystem_ex01では最もシンプルな２次カーブを用いる。
*ユーザー定義のカーブfunctionを用いて呼び出すことも可能。
機械回転数 [rpm]
体積流量 [m]
揚程 [m]
{定格回転数, 定格体積流量}
{定格回転数, 定格揚程}
機械回転数 [rpm]
redeclare function flowCharacteristic = Modelica.Fluid.Machines.BaseClasses.PumpCharacteristics.quadraticFlow(V_flow_nominal = {0, 0.25, 0.5}, head_nominal = {100, 60, 0})
定格点のparameterを基に
体積流量=k*機械回転数
として算出(スケール)される。
定格点のparameterを基に
体積流量=k*(機械回転数)^2
として算出（スケール）される。
非定格点の体積流量、揚程の算出
体積流量、揚程の特性の与え方
下記の記述により、特性モデルにMSL収録の２次カーブfunctionを用いることを設定すると共に、２次カーブを成す３点の値をparameterとして与える

## Slide 33
断熱効率特性の与え方
体積流量 [m^3/s]
断熱効率 [nond]
定格回転数における効率カーブを与える。
MSLには効率を一定とするfunctionしか用意されていないため、カーブを与えたい場合はユーザー定義functionを作成する必要が有る。
pumpingSystem_ex01では、簡略化のため、定格回転数における断熱効率を一定とするようparameter設定する。
redeclare function efficiencyCharacteristic = Modelica.Fluid.Machines.BaseClasses.PumpCharacteristics.constantEfficiency(eta_nominal = 0.9)
下記の記述により、特性モデルに効率固定値のfunctionを用いることを設定すると共に、固定値として設定する効率値を与える。

## Slide 34
pumpingSystem_ex02

## Slide 36
pumpingSystem_ex03

## Slide 37
“Prescribed pump” is replaced with “pump”
The valve for flow control is added. The valve type is the simplest one.
The components so as to provide mechanical rotational speed (in [rpm]) to flange connector are added.

## Slide 38
Input:
mechanical rotary speed of pump.

## Slide 39
Input:
opening of linear valve.

## Slide 40
Output:
Volumetric flow rate through pump.

## Slide 41
Output:
Pump’s volumetric flow rate vs. mechanical rotation speed.

## Slide 42
Output:
pump discharge pressure.

## Slide 43
Output:
Mechanical power consumed by pump.

## Slide 44
Output:
Torque into flange of pump.

## Slide 45
Output:
mechanical power consumption of pump vs. mechanical rotation speed.

## Slide 46
Output:
pressure difference of valve vs. mass flow rate via valve.
Increase in pump rotation speed.
Close of valve (from 1 to 0.5).
If pump speed is reduced.
If pump speed is increased.

## Slide 48
Pipe= Flow resistance.
-. Fluid pressure drops through it.
Input (boundary cond.):
-. mass flow rate with ramp in time. Increase it gradually.
-. Inlet temperature with fixed value.
Input (boundary cond.):
-. Outlet pressure with fixed value.
Output of interest:
-. Inlet pressure.
Volumes
-. In order to see the temperature and enthalpy change across the pipe.
Output of interest:
-. Outlet temperature.

## Slide 49
Input:
mass flow rate flowing through pipe.

## Slide 50
Output:
Fluid pressure of pipe inlet.
It increases as mass flow rate increases.

## Slide 51
Output:
Specific enthalpy at inlet.
Output:
Specific enthalpy at outlet.
It is same value as inlet owe to enthalpy conservation.
The “delay” occurs due to volume effect (storage of mass and energy).

## Slide 52
Output:
Temperature at inlet.
Output:
-. Temperature at outlet.
-. It is slightly greater than that of inlet. The energy lost as pressure drop is converted to temperature. Notice flow enthalpy conserves because the energy lost does not go anywhere.
-. Temperature rise occurs only in incompressible fluid (liquid)
-. The temperature difference increases as pressure drop increases.